## Template
1	1	1	R	0x03	ID	xxx	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;

## Common
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model common (1)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model common (1)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	18	16	R	0x03	Mn	Manufacturer	string		string	string	string	string	string	string	string	string		char Mn[32];
19	34	16	R	0x03	Md	Device	string		string	string	string	string	string	string	string	string		char Md[32];
35	42	8	R	0x03	Opt	Options	string		string	string	string	string	string	string	string	string		char Opt[16];
43	50	8	R	0x03	Vr	SW version of inverter	string		string	string	string	string	string	string	string	string		char Vr[16];
51	66	16	R	0x03	SN	Serialnumber of the inverter	string		string	string	string	string	string	string	string	string		char SN[32];
67	67	1	R	0x03	DA	Modbus Device Address	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t DA;

## Inverter
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model inverter (10x)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model inverter (10x)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	R	0x03	A	AC Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t A;
4	4	1	R	0x03	AphA	Phase A Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t AphA;
5	5	1	R	0x03	AphB	Phase B Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t AphB;
6	6	1	R	0x03	AphC	Phase C Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t AphC;
7	7	1	R	0x03	A_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t A_SF;
8	8	1	R	0x03	PPVphAB	Phase Voltage AB	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t PPVphAB;
9	9	1	R	0x03	PPVphBC	Phase Voltage BC	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t PPVphBC;
10	10	1	R	0x03	PPVphCA	Phase Voltage CA	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t PPVphCA;
11	11	1	R	0x03	PhVphA	Phase Voltage AN	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t PhVphA;
12	12	1	R	0x03	PhVphB	Phase Voltage BN	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t PhVphB;
13	13	1	R	0x03	PhVphC	Phase Voltage CN	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t PhVphC;
14	14	1	R	0x03	V_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t V_SF;
15	15	1	R	0x03	W	AC Power	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t W;
16	16	1	R	0x03	W_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t W_SF;
17	17	1	R	0x03	Hz	Line Frequency	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t Hz;
18	18	1	R	0x03	Hz_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t Hz_SF;
19	19	1	R	0x03	VA	AC Apparent Power	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VA;
20	20	1	R	0x03	VA_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VA_SF;
21	21	1	R	0x03	VAr	AC Reactive Power	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAr;
22	22	1	R	0x03	VAr_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAr_SF;
23	23	1	R	0x03	PF	AC Power Factor	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PF;
24	24	1	R	0x03	PF_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PF_SF;
25	26	2	R	0x03	WH	AC Energy	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t WH;
27	27	1	R	0x03	WH_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WH_SF;
28	28	1	R	0x03	DCA	DC Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t DCA;
29	29	1	R	0x03	DCA_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCA_SF;
30	30	1	R	0x03	DCV	DC Voltage	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t DCV;
31	31	1	R	0x03	DCV_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCV_SF;
32	32	1	R	0x03	DCW	DC Power	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCW;
33	33	1	R	0x03	DCW_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCW_SF;
34	34	1	R	0x03	TmpCab	Cabinet Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t TmpCab;
35	35	1	R	0x03	TmpSnk	Heat Sink Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t TmpSnk;
36	36	1	R	0x03	TmpTrns	Transformer Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t TmpTrns;
37	37	1	R	0x03	TmpOt	Other Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t TmpOt;
38	38	1	R	0x03	Tmp_SF		sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t Tmp_SF;
39	39	1	R	0x03	St	Enumerated value. Operating state	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t St;
40	40	1	R	0x03	StVnd	Vendor specific operating state code	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t StVnd;
41	42	2	R	0x03	Evt1	Bitmask value. Event fields	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t Evt1;
43	44	2	R	0x03	Evt2	Reserved for future use	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t Evt2;
45	46	2	R	0x03	EvtVnd1	Vendor defined events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t EvtVnd1;
47	48	2	R	0x03	EvtVnd2	Vendor defined events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t EvtVnd2;
49	50	2	R	0x03	EvtVnd3	Vendor defined events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t EvtVnd3;
51	52	2	R	0x03	EvtVnd4	Vendor defined events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t EvtVnd4;

## Nameplate
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model nameplate (120)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model nameplate (120)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	R	0x03	DERTyp	Type of DER device. Default value is 4 to indicate PV device.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t DERTyp;
4	4	1	R	0x03	WRtg	Continuous power output capability of the inverter.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WRtg;
5	5	1	R	0x03	WRtg_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WRtg_SF;
6	6	1	R	0x03	VARtg	Continuous Volt-Ampere capability of the inverter.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VARtg;
7	7	1	R	0x03	VARtg_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VARtg_SF;
8	8	1	R	0x03	VArRtgQ1	Continuous VAR capability of the inverter in quadrant 1.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArRtgQ1;
9	9	1	R	0x03	VArRtgQ2	Continuous VAR capability of the inverter in quadrant 2.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArRtgQ2;
10	10	1	R	0x03	VArRtgQ3	Continuous VAR capability of the inverter in quadrant 3.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArRtgQ3;
11	11	1	R	0x03	VArRtgQ4	Continuous VAR capability of the inverter in quadrant 4.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArRtgQ4;
12	12	1	R	0x03	VArRtg_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArRtg_SF;
13	13	1	R	0x03	ARtg	Maximum RMS AC current level capability of the inverter.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ARtg;
14	14	1	R	0x03	ARtg_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t ARtg_SF;
15	15	1	R	0x03	PFRtgQ1	Minimum power factor capability of the inverter in quadrant 1.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFRtgQ1;
16	16	1	R	0x03	PFRtgQ2	Minimum power factor capability of the inverter in quadrant 2.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFRtgQ2;
17	17	1	R	0x03	PFRtgQ3	Minimum power factor capability of the inverter in quadrant 3.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFRtgQ3;
18	18	1	R	0x03	PFRtgQ4	Minimum power factor capability of the inverter in quadrant 4.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFRtgQ4;
19	19	1	R	0x03	PFRtg_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFRtg_SF;
20	20	1	R	0x03	WHRtg	Nominal energy rating of storage device.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WHRtg;
21	21	1	R	0x03	WHRtg_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WHRtg_SF;
22	22	1	R	0x03	AhrRtg	The usable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t AhrRtg;
23	23	1	R	0x03	AhrRtg_SF	Scale factor for amp-hour rating.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t AhrRtg_SF;
24	24	1	R	0x03	MaxChaRte	Maximum rate of energy transfer into the storage device.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t MaxChaRte;
25	25	1	R	0x03	MaxChaRte_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t MaxChaRte_SF;
26	26	1	R	0x03	MaxDisChaRte	Maximum rate of energy transfer out of the storage device.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t MaxDisChaRte;
27	27	1	R	0x03	MaxDisChaRte_SF	Scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t MaxDisChaRte_SF;
28	28	1	R	0x03	Pad	Pad register.	pad		pad	pad	pad	pad	pad	pad	pad	pad		pad Pad;

## Settings
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model settings (121)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model settings (121)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	R	0x03	WMax	Setting for maximum power output. Default to WRtg.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WMax;
4	4	1	R	0x03	VRef	Voltage at the PCC.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VRef;
5	5	1	R	0x03	VRefOfs	Offset from PCC to inverter.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VRefOfs;
6	6	1	R	0x03	VMax	Setpoint for maximum voltage.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VMax;
7	7	1	R	0x03	VMin	Setpoint for minimum voltage.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VMin;
8	8	1	R	0x03	VAMax	Setpoint for maximum apparent power. Default to VARtg.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VAMax;
9	9	1	R	0x03	VArMaxQ1	Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArMaxQ1;
10	10	1	R	0x03	VArMaxQ2	Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArMaxQ2;
11	11	1	R	0x03	VArMaxQ3	Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArMaxQ3;
12	12	1	R	0x03	VArMaxQ4	Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArMaxQ4;
13	13	1	R	0x03	WGra	Default ramp rate of change of active power due to command or internal action.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WGra;
14	14	1	R	0x03	PFMinQ1	Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFMinQ1;
15	15	1	R	0x03	PFMinQ2	Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFMinQ2;
16	16	1	R	0x03	PFMinQ3	Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFMinQ3;
17	17	1	R	0x03	PFMinQ4	Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFMinQ4;
18	18	1	R	0x03	VArAct	VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VArAct;
19	19	1	R	0x03	ClcTotVA	Calculation method for total apparent power. 1=vector 2=arithmetic.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ClcTotVA;
20	20	1	R	0x03	MaxRmpRte	Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t MaxRmpRte;
21	21	1	R	0x03	ECPNomHz	Setpoint for nominal frequency at the ECP.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ECPNomHz;
22	22	1	R	0x03	ConnPh	Identity of connected phase for single phase inverters. A=1 B=2 C=3.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ConnPh;
23	23	1	R	0x03	WMax_SF	Scale factor for real power.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WMax_SF;
24	24	1	R	0x03	VRef_SF	Scale factor for voltage at the PCC.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VRef_SF;
25	25	1	R	0x03	VRefOfs_SF	Scale factor for offset voltage.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VRefOfs_SF;
26	26	1	R	0x03	VMinMax_SF	Scale factor for min/max voltages.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VMinMax_SF;
27	27	1	R	0x03	VAMax_SF	Scale factor for apparent power.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAMax_SF;
28	28	1	R	0x03	VArMax_SF	Scale factor for reactive power.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArMax_SF;
29	29	1	R	0x03	WGra_SF	Scale factor for default ramp rate.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WGra_SF;
30	30	1	R	0x03	PFMin_SF	Scale factor for minimum power factor.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFMin_SF;
31	31	1	R	0x03	MaxRmpRte_SF	Scale factor for maximum ramp percentage.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t MaxRmpRte_SF;
32	32	1	R	0x03	ECPNomHz_SF	Scale factor for nominal frequency.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t ECPNomHz_SF;

## Status
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model status (122)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model status (122)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	R	0x03	PVConn	PV inverter present/available status. Enumerated value.	bitfield16		bitfield16	bitfield16	bitfield16	bitfield16	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t PVConn;
4	4	1	R	0x03	StorConn	Storage inverter present/available status. Enumerated value.	bitfield16		bitfield16	bitfield16	bitfield16	bitfield16	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t StorConn;
5	5	1	R	0x03	ECPConn	ECP connection status: disconnected=0 connected=1.	bitfield16		bitfield16	bitfield16	bitfield16	bitfield16	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ECPConn;
6	9	4	R	0x03	ActWh	AC lifetime active (real) energy output.	acc64		acc64	acc64	acc64	acc64	acc64	acc64	acc64	uint64_t		uint64_t ActWh;
10	13	4	R	0x03	ActVAh	AC lifetime apparent energy output.	acc64		acc64	acc64	acc64	acc64	acc64	acc64	acc64	uint64_t		uint64_t ActVAh;
14	17	4	R	0x03	ActVArhQ1	AC lifetime reactive energy output in quadrant 1.	acc64		acc64	acc64	acc64	acc64	acc64	acc64	acc64	uint64_t		uint64_t ActVArhQ1;
18	21	4	R	0x03	ActVArhQ2	AC lifetime reactive energy output in quadrant 2.	acc64		acc64	acc64	acc64	acc64	acc64	acc64	acc64	uint64_t		uint64_t ActVArhQ2;
22	25	4	R	0x03	ActVArhQ3	AC lifetime negative energy output in quadrant 3.	acc64		acc64	acc64	acc64	acc64	acc64	acc64	acc64	uint64_t		uint64_t ActVArhQ3;
26	29	4	R	0x03	ActVArhQ4	AC lifetime reactive energy output in quadrant 4.	acc64		acc64	acc64	acc64	acc64	acc64	acc64	acc64	uint64_t		uint64_t ActVArhQ4;
30	30	1	R	0x03	VArAval	Amount of VARs available without impacting watts output.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArAval;
31	31	1	R	0x03	VArAval_SF	Scale factor for available VARs.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArAval_SF;
32	32	1	R	0x03	WAval	Amount of Watts available.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WAval;
33	33	1	R	0x03	WAval_SF	Scale factor for available Watts.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WAval_SF;
34	35	2	R	0x03	StSetLimMsk	Bit Mask indicating setpoint limit(s) reached.	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t StSetLimMsk;
36	37	2	R	0x03	StActCtl	Bit Mask indicating which inverter controls are currently active.	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t StActCtl;
38	41	4	R	0x03	TmSrc	Source of time synchronization.	string		string	string	string	string	string	string	string	string		char TmSrc[8];
42	43	2	R	0x03	Tms	Seconds since 01-01-2000 00:00 UTC	uint32		uint32	uint32	uint32	uint32	uint32	uint32	uint32	uint32		uint32 Tms;
44	44	1	R	0x03	RtSt	Bit Mask indicating active ride-through status.	bitfield16		bitfield16	bitfield16	bitfield16	bitfield16	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t RtSt;
45	45	1	R	0x03	Ris	Isolation resistance.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t Ris;
46	46	1	R	0x03	Ris_SF	Scale factor for isolation resistance.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t Ris_SF;

## Controls
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model controls (123)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model controls (123)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	RW	0x03 / 0x06 / 0x10	Conn_WinTms	Time window for connect/disconnect.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t Conn_WinTms;
4	4	1	RW	0x03 / 0x06 / 0x10	Conn_RvrtTms	Timeout period for connect/disconnect.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t Conn_RvrtTms;
5	5	1	RW	0x03 / 0x06 / 0x10	Conn	Enumerated valued. Connection control.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t Conn;
6	6	1	RW	0x03 / 0x06 / 0x10	WMaxLimPct	Set power output to specified level.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WMaxLimPct;
7	7	1	RW	0x03 / 0x06 / 0x10	WMaxLimPct_WinTms	Time window for power limit change.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WMaxLimPct_WinTms;
8	8	1	RW	0x03 / 0x06 / 0x10	WMaxLimPct_RvrtTms	Timeout period for power limit.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WMaxLimPct_RvrtTms;
9	9	1	RW	0x03 / 0x06 / 0x10	WMaxLimPct_RmpTms	Ramp time for moving from current setpoint to new setpoint.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WMaxLimPct_RmpTms;
10	10	1	RW	0x03 / 0x06 / 0x10	WMaxLim_Ena	Enumerated valued. Throttle enable/disable control.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WMaxLim_Ena;
11	11	1	RW	0x03 / 0x06 / 0x10	OutPFSet	Set power factor to specific value - cosine of angle.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t OutPFSet;
12	12	1	RW	0x03 / 0x06 / 0x10	OutPFSet_WinTms	Time window for power factor change.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t OutPFSet_WinTms;
13	13	1	RW	0x03 / 0x06 / 0x10	OutPFSet_RvrtTms	Timeout period for power factor.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t OutPFSet_RvrtTms;
14	14	1	RW	0x03 / 0x06 / 0x10	OutPFSet_RmpTms	Ramp time for moving from current setpoint to new setpoint.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t OutPFSet_RmpTms;
15	15	1	RW	0x03 / 0x06 / 0x10	OutPFSet_Ena	Enumerated valued. Fixed power factor enable/disable control.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t OutPFSet_Ena;
16	16	1	R	0x03	VArWMaxPct	Reactive power in percent of WMax.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArWMaxPct;
17	17	1	RW	0x03 / 0x06 / 0x10	VArMaxPct	Reactive power in percent of VArMax.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArMaxPct;
18	18	1	R	0x03	VArAvalPct	Reactive power in percent of VArAval.	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArAvalPct;
19	19	1	RW	0x03 / 0x06 / 0x10	VArPct_WinTms	Time window for VAR limit change.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VArPct_WinTms;
20	20	1	RW	0x03 / 0x06 / 0x10	VArPct_RvrtTms	Timeout period for VAR limit.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VArPct_RvrtTms;
21	21	1	RW	0x03 / 0x06 / 0x10	VArPct_RmpTms	Ramp time for moving from current setpoint to new setpoint.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VArPct_RmpTms;
22	22	1	R	0x03	VArPct_Mod	Enumerated value. VAR percent limit mode.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VArPct_Mod;
23	23	1	RW	0x03 / 0x06 / 0x10	VArPct_Ena	Enumerated valued. Percent limit VAr enable/disable control.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VArPct_Ena;
24	24	1	R	0x03	WMaxLimPct_SF	Scale factor for power output percent.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WMaxLimPct_SF;
25	25	1	R	0x03	OutPFSet_SF	Scale factor for power factor.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t OutPFSet_SF;
26	26	1	R	0x03	VArPct_SF	Scale factor for reactive power percent.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VArPct_SF;

## MPPT
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model mppt (160)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model mppt (160)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	R	0x03	DCA_SF	Current Scale Factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCA_SF;
4	4	1	R	0x03	DCV_SF	Voltage Scale Factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCV_SF;
5	5	1	R	0x03	DCW_SF	Power Scale Factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCW_SF;
6	6	1	R	0x03	DCWH_SF	Energy Scale Factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t DCWH_SF;
7	8	2	R	0x03	Evt	Global Events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t Evt;
9	9	1	R	0x03	N	Number of Modules	count		count	count	count	count	count	count	count	count		count N;
10	10	1	R	0x03	TmsPer	Timestamp Period	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t TmsPer;
11	11	1	R	0x03	module/1/ID	Input ID	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/1/ID;
12	19	8	R	0x03	module/1/IDStr	Input ID Sting	string		string	string	string	string	string	string	string	string		char module/1/IDStr[16];
20	20	1	R	0x03	module/1/DCA	DC Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/1/DCA;
21	21	1	R	0x03	module/1/DCV	DC Voltage	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/1/DCV;
22	22	1	R	0x03	module/1/DCW	DC Power	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/1/DCW;
23	24	2	R	0x03	module/1/DCWH	Lifetime Energy	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t module/1/DCWH;
25	26	2	R	0x03	module/1/Tms	Timestamp	uint32		uint32	uint32	uint32	uint32	uint32	uint32	uint32	uint32		uint32 module/1/Tms;
27	27	1	R	0x03	module/1/Tmp	Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t module/1/Tmp;
28	28	1	R	0x03	module/1/DCSt	Operating State	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/1/DCSt;
29	30	2	R	0x03	module/1/DCEvt	Module Events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t module/1/DCEvt;
31	31	1	R	0x03	module/2/ID	Input ID	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/2/ID;
32	39	8	R	0x03	module/2/IDStr	Input ID Sting	string		string	string	string	string	string	string	string	string		char module/2/IDStr[16];
40	40	1	R	0x03	module/2/DCA	DC Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/2/DCA;
41	41	1	R	0x03	module/2/DCV	DC Voltage	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/2/DCV;
42	42	1	R	0x03	module/2/DCW	DC Power	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/2/DCW;
43	44	2	R	0x03	module/2/DCWH	Lifetime Energy	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t module/2/DCWH;
45	46	2	R	0x03	module/2/Tms	Timestamp	uint32		uint32	uint32	uint32	uint32	uint32	uint32	uint32	uint32		uint32 module/2/Tms;
47	47	1	R	0x03	module/2/Tmp	Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t module/2/Tmp;
48	48	1	R	0x03	module/2/DCSt	Operating State	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/2/DCSt;
49	50	2	R	0x03	module/2/DCEvt	Module Events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t module/2/DCEvt;
51	51	1	R	0x03	module/3/ID	Input ID	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/3/ID;
52	59	8	R	0x03	module/3/IDStr	Input ID Sting	string		string	string	string	string	string	string	string	string		char module/3/IDStr[16];
60	60	1	R	0x03	module/3/DCA	DC Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/3/DCA;
61	61	1	R	0x03	module/3/DCV	DC Voltage	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/3/DCV;
62	62	1	R	0x03	module/3/DCW	DC Power	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/3/DCW;
63	64	2	R	0x03	module/3/DCWH	Lifetime Energy	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t module/3/DCWH;
65	66	2	R	0x03	module/3/Tms	Timestamp	uint32		uint32	uint32	uint32	uint32	uint32	uint32	uint32	uint32		uint32 module/3/Tms;
67	67	1	R	0x03	module/3/Tmp	Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t module/3/Tmp;
68	68	1	R	0x03	module/3/DCSt	Operating State	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/3/DCSt;
69	70	2	R	0x03	module/3/DCEvt	Module Events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t module/3/DCEvt;
71	71	1	R	0x03	module/4/ID	Input ID	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/4/ID;
72	79	8	R	0x03	module/4/IDStr	Input ID Sting	string		string	string	string	string	string	string	string	string		char module/4/IDStr[16];
80	80	1	R	0x03	module/4/DCA	DC Current	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/4/DCA;
81	81	1	R	0x03	module/4/DCV	DC Voltage	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/4/DCV;
82	82	1	R	0x03	module/4/DCW	DC Power	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/4/DCW;
83	84	2	R	0x03	module/4/DCWH	Lifetime Energy	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t module/4/DCWH;
85	86	2	R	0x03	module/4/Tms	Timestamp	uint32		uint32	uint32	uint32	uint32	uint32	uint32	uint32	uint32		uint32 module/4/Tms;
87	87	1	R	0x03	module/4/Tmp	Temperature	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t module/4/Tmp;
88	88	1	R	0x03	module/4/DCSt	Operating State	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t module/4/DCSt;
89	90	2	R	0x03	module/4/DCEvt	Module Events	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t module/4/DCEvt;

## Storage
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model storage (124)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model storage (124)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	R	0x03	WChaMax	Setpoint for maximum charge. / Additional Fronius description: / Reference Value for maximum Charge and Discharge. / Multiply this value by InWRte to define maximum charging and OutWRte to define maximum discharging. / Every rate between this two limits is allowed. / The inverter is not fully capable of transferring power as reported by this reference value. / Note that InWRte and OutWRte can be negative to define ranges for charging and discharging only	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WChaMax;
4	4	1	R	0x03	WChaGra	Setpoint for maximum charging rate. Default is MaxChaRte.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WChaGra;
5	5	1	R	0x03	WDisChaGra	Setpoint for maximum discharge rate. Default is MaxDisChaRte.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t WDisChaGra;
6	6	1	RW	0x03 / 0x06 / 0x10	StorCtl_Mod	Activate hold/discharge/charge storage control mode. Bitfield value. / Additional Fronius description: / Active hold/discharge/charge storage control mode. / Set the charge field to enable charging and the discharge field to enable discharging.	bitfield16		bitfield16	bitfield16	bitfield16	bitfield16	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t StorCtl_Mod;
7	7	1	RW	0x03 / 0x06 / 0x10	VAChaMax	Setpoint for maximum charging VA.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t VAChaMax;
8	8	1	RW	0x03 / 0x06 / 0x10	MinRsvPct	Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t MinRsvPct;
9	9	1	R	0x03	ChaState	Currently available energy as a percent of the capacity rating.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ChaState;
10	10	1	R	0x03	StorAval	State of charge (ChaState) minus storage reserve (MinRsvPct) times capacity rating (AhrRtg).	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t StorAval;
11	11	1	R	0x03	InBatV	Internal battery voltage.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t InBatV;
12	12	1	R	0x03	ChaSt	Charge status of storage device. Enumerated value.	enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ChaSt;
13	13	1	RW	0x03 / 0x06 / 0x10	OutWRte	Percent of max discharge rate. / Additional Fronius description: / Defines maximum Discharge rate. If not used than the default is 100 and WChaMax defines max. Discharge rate. / See WChaMax for details	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t OutWRte;
14	14	1	RW	0x03 / 0x06 / 0x10	InWRte	Percent of max charging rate. / Additional Fronius description: / Defines maximum Charge rate. If not used than the default is 100 and WChaMax defines max. Charge rate. / See WChaMax for details	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t InWRte;
15	15	1	R	0x03	InOutWRte_WinTms	Time window for charge/discharge rate change.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t InOutWRte_WinTms;
16	16	1	RW	0x03 / 0x06 / 0x10	InOutWRte_RvrtTms	Timeout period for charge/discharge rate.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t InOutWRte_RvrtTms;
17	17	1	R	0x03	InOutWRte_RmpTms	Ramp time for moving from current setpoint to new setpoint.	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t InOutWRte_RmpTms;
18	18	1	RW	0x03 / 0x06 / 0x10	ChaGriSet		enum16		enum16	enum16	enum16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ChaGriSet;
19	19	1	R	0x03	WChaMax_SF	Scale factor for maximum charge.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WChaMax_SF;
20	20	1	R	0x03	WChaDisChaGra_SF	Scale factor for maximum charge and discharge rate.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WChaDisChaGra_SF;
21	21	1	R	0x03	VAChaMax_SF	Scale factor for maximum charging VA.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAChaMax_SF;
22	22	1	R	0x03	MinRsvPct_SF	Scale factor for minimum reserve percentage.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t MinRsvPct_SF;
23	23	1	R	0x03	ChaState_SF	Scale factor for available energy percent.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t ChaState_SF;
24	24	1	R	0x03	StorAval_SF	Scale factor for state of charge.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t StorAval_SF;
25	25	1	R	0x03	InBatV_SF	Scale factor for battery voltage.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t InBatV_SF;
26	26	1	R	0x03	InOutWRte_SF	Scale factor for percent charge/discharge rate.	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t InOutWRte_SF;

## Meter
1	1	1	R	0x03	ID	Well-known value. Uniquely identifies this as a sunspec model ac_meter (20x)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t ID;
2	2	1	R	0x03	L	Length of sunspec model ac_meter (20x)	uint16		uint16	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t	uint16_t		uint16_t L;
3	3	1	R	0x03	A	Total AC Current	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t A;
4	4	1	R	0x03	AphA	Phase A Current	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t AphA;
5	5	1	R	0x03	AphB	Phase B Current	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t AphB;
6	6	1	R	0x03	AphC	Phase C Current	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t AphC;
7	7	1	R	0x03	A_SF	Current scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t A_SF;
8	8	1	R	0x03	PhV	Line to Neutral AC Voltage (average of active phases)	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PhV;
9	9	1	R	0x03	PhVphA	Phase Voltage AN	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PhVphA;
10	10	1	R	0x03	PhVphB	Phase Voltage BN	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PhVphB;
11	11	1	R	0x03	PhVphC	Phase Voltage CN	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PhVphC;
12	12	1	R	0x03	PPV	Line to Line AC Voltage (average of active phases)	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PPV;
13	13	1	R	0x03	PhVphAB	Phase Voltage AB	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PhVphAB;
14	14	1	R	0x03	PhVphBC	Phase Voltage BC	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PhVphBC;
15	15	1	R	0x03	PhVphCA	Phase Voltage CA	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PhVphCA;
16	16	1	R	0x03	V_SF	Voltage scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t V_SF;
17	17	1	R	0x03	Hz	Frequency	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t Hz;
18	18	1	R	0x03	Hz_SF	Frequency scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t Hz_SF;
19	19	1	R	0x03	W	Total Real Power	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t W;
20	20	1	R	0x03	WphA	Watts phase A	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WphA;
21	21	1	R	0x03	WphB	Watts phase B	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WphB;
22	22	1	R	0x03	WphC	Watts phase C	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t WphC;
23	23	1	R	0x03	W_SF	Real Power scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t W_SF;
24	24	1	R	0x03	VA	AC Apparent Power	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VA;
25	25	1	R	0x03	VAphA	VA phase A	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAphA;
26	26	1	R	0x03	VAphB	VA phase B	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAphB;
27	27	1	R	0x03	VAphC	VA phase C	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAphC;
28	28	1	R	0x03	VA_SF	Apparent Power scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VA_SF;
29	29	1	R	0x03	VAR	Reactive Power	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAR;
30	30	1	R	0x03	VARphA	VAR phase A	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VARphA;
31	31	1	R	0x03	VARphB	VAR phase B	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VARphB;
32	32	1	R	0x03	VARphC	VAR phase C	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VARphC;
33	33	1	R	0x03	VAR_SF	Reactive Power scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t VAR_SF;
34	34	1	R	0x03	PF	Power Factor	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PF;
35	35	1	R	0x03	PFphA	PF phase A	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFphA;
36	36	1	R	0x03	PFphB	PF phase B	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFphB;
37	37	1	R	0x03	PFphC	PF phase C	int16		int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PFphC;
38	38	1	R	0x03	PF_SF	Power Factor scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t PF_SF;
39	40	2	R	0x03	TotWhExp	Total Real Energy Exported	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhExp;
41	42	2	R	0x03	TotWhExpPhA	Total Watt-hours Exported phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhExpPhA;
43	44	2	R	0x03	TotWhExpPhB	Total Watt-hours Exported phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhExpPhB;
45	46	2	R	0x03	TotWhExpPhC	Total Watt-hours Exported phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhExpPhC;
47	48	2	R	0x03	TotWhImp	Total Real Energy Imported	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhImp;
49	50	2	R	0x03	TotWhImpPhA	Total Watt-hours Imported phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhImpPhA;
51	52	2	R	0x03	TotWhImpPhB	Total Watt-hours Imported phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhImpPhB;
53	54	2	R	0x03	TotWhImpPhC	Total Watt-hours Imported phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotWhImpPhC;
55	55	1	R	0x03	TotWh_SF	Real Energy scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t TotWh_SF;
56	57	2	R	0x03	TotVAhExp	Total Apparent Energy Exported	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhExp;
58	59	2	R	0x03	TotVAhExpPhA	Total VA-hours Exported phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhExpPhA;
60	61	2	R	0x03	TotVAhExpPhB	Total VA-hours Exported phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhExpPhB;
62	63	2	R	0x03	TotVAhExpPhC	Total VA-hours Exported phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhExpPhC;
64	65	2	R	0x03	TotVAhImp	Total Apparent Energy Imported	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhImp;
66	67	2	R	0x03	TotVAhImpPhA	Total VA-hours Imported phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhImpPhA;
68	69	2	R	0x03	TotVAhImpPhB	Total VA-hours Imported phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhImpPhB;
70	71	2	R	0x03	TotVAhImpPhC	Total VA-hours Imported phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVAhImpPhC;
72	72	1	R	0x03	TotVAh_SF	Apparent Energy scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t TotVAh_SF;
73	74	2	R	0x03	TotVArhImpQ1	Total Reactive Energy Imported Quadrant 1	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ1;
75	76	2	R	0x03	TotVArhImpQ1PhA	Total VAr-hours Imported Q1 phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ1PhA;
77	78	2	R	0x03	TotVArhImpQ1PhB	Total VAr-hours Imported Q1 phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ1PhB;
79	80	2	R	0x03	TotVArhImpQ1PhC	Total VAr-hours Imported Q1 phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ1PhC;
81	82	2	R	0x03	TotVArhImpQ2	Total Reactive Power Imported Quadrant 2	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ2;
83	84	2	R	0x03	TotVArhImpQ2PhA	Total VAr-hours Imported Q2 phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ2PhA;
85	86	2	R	0x03	TotVArhImpQ2PhB	Total VAr-hours Imported Q2 phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ2PhB;
87	88	2	R	0x03	TotVArhImpQ2PhC	Total VAr-hours Imported Q2 phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhImpQ2PhC;
89	90	2	R	0x03	TotVArhExpQ3	Total Reactive Power Exported Quadrant 3	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ3;
91	92	2	R	0x03	TotVArhExpQ3PhA	Total VAr-hours Exported Q3 phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ3PhA;
93	94	2	R	0x03	TotVArhExpQ3PhB	Total VAr-hours Exported Q3 phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ3PhB;
95	96	2	R	0x03	TotVArhExpQ3PhC	Total VAr-hours Exported Q3 phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ3PhC;
97	98	2	R	0x03	TotVArhExpQ4	Total Reactive Power Exported Quadrant 4	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ4;
99	100	2	R	0x03	TotVArhExpQ4PhA	Total VAr-hours Exported Q4 Imported phase A	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ4PhA;
101	102	2	R	0x03	TotVArhExpQ4PhB	Total VAr-hours Exported Q4 Imported phase B	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ4PhB;
103	104	2	R	0x03	TotVArhExpQ4PhC	Total VAr-hours Exported Q4 Imported phase C	acc32		acc32	acc32	acc32	acc32	acc32	acc32	uint32_t	uint32_t		uint32_t TotVArhExpQ4PhC;
105	105	1	R	0x03	TotVArh_SF	Reactive Energy scale factor	sunssf		sunssf	sunssf	int16_t	int16_t	int16_t	int16_t	int16_t	int16_t		int16_t TotVArh_SF;
106	107	2	R	0x03	Evt	Meter Event Flags	bitfield32		bitfield32	bitfield32	bitfield32	bitfield32	bitfield32	uint32_t	uint32_t	uint32_t		uint32_t Evt;